Faculty of Engineering, Architecture and Science

Department of Mechanical, Industrial, and Mechatronics Engineering

| Program | Electrical Engineering |
| --- | --- |
| Course Number | ELE746 |
| Course Title | Power Systems Analysis |
| Semester/Year | F2025 |
| Instructor | Dr. Mohammadreza Arani |

| Lab/Tutorial Report NO. | Lab #2 |
| --- | --- |

| Report Title | Project 2: Three-Phase Symmetrical Faults |
| --- | --- |

| Section No. | 02 |
| --- | --- |
| Submission Date | November 21, 2025 |
| Due Date | November 21, 2025 |

| Name | Student ID | Signature* |
| --- | --- | --- |
| Shai Mourad | 501170415 |  |

*By signing above you attest that you have contributed to this submission and confirm that all

work you have contributed to this submission is your own work. Any suspicion of copying or

plagiarism in this work will result in an investigation of Academic Misconduct and may result

in a “0” on the work, an “F” in the course, or possibly more severe penalties, as well as a

Disciplinary Notice on your academic record under the Student Code of Academic Conduct,

which can be found online at:

https://www.torontomu.ca/senate/policies/pol60.pdf.

## Table of Contents

Pre-Lab………………………………………………………………...2

Post-Lab:

- Introduction……………………………………………………..4

- Objectives…………………………………………………….…4

- Results………………………………………………………...…5

- Discussion………………………………………………………6

- Conclusion………………………………………………………6

- References………………………………………………………6

## Pre-Lab

## Post-Lab

#### Introduction

This lab analyzes a three-phase balanced symmetrical fault in a multimachine power system and then compares the calculated values to software simulations using ETAP. The most severe type of short circuit, a symmetrical fault, produces the highest fault current and stresses on equipment. Therefore, accuracy of analysis is extremely important when designing protection systems, selecting circuit breakers, or ensuring system stability.

The system in this lab has three synchronous generators connected to a high voltage network through step-up transformers, three transmission lines, and a bolted three-phase fault applied at Bus 2. Calculations were completed in per-unit using a base power found from the student ID, while all generator voltages were assumed to be 1.0 pu with equal phase angles as required for worst-case subtransient fault analysis.

#### Objectives

- To construct the per-unit impedance diagram of the three-machine power system using the system base derived from the student ID number.

- To manually compute the Thevenin equivalent impedance and subtransient fault current at Bus 2.

- To determine the individual current contributions from each generator through the transmission lines.

- To simulate the same balanced three-phase fault using ETAP’s short-circuit analysis module.

- To compare ETAP results with manually calculated values and discuss any discrepancies.

#### Results

Figure 1 - ETAP Circuit Simulation Result

| Quantity (Bus / branch) | Pre-lab | ETAP |
| --- | --- | --- |
| Total 3-phase fault current at Bus 2 | 8.15 kA | 5.721 kA |
| Gen1 contribution to fault | 3.40 kA | 1.443 kA |
| Gen2 contribution to fault | 2.65 kA | 2.014 kA |
| Gen3 contribution to fault | 2.12 kA | 2.264 kA |

Table 1 - Observations and Results from ETAP Circuit

#### Discussion

Despite numerical differences, the qualitative behaviour of the system is consistent between pre-lab calculations and in-lab results. ETAP shows the same distribution of currents among the generators and confirms the topology-driven division of fault current based on relative series reactances. Due to using different base values in the pre-lab vs the simulations (a base using one’s student ID is calculated and used in the pre-lab but not simulations, which have pre-set values to use), the magnitudes cannot be directly compared.

The exercise reaffirms that manual per-unit analysis correctly predicts the structure and relative magnitude of fault contributions. Once ETAP’s base is identified and the values are converted, the results are expected to align closely with the manual values.

#### Conclusion

Both using manual and simulated methods, this lab properly demonstrated symmetrical fault analysis. Manual calculations provided a worst-case estimate based on simplified assumptions and a custom student-ID system base, while ETAP had consistent patterns of current distributions. Due to internal base differences, the values were different but showed similar patterns.

The lab shows the significance of consistent base usage in per-unit analysis, and how they can alter the results greatly while still showing similar output patterns. If the base values were the same, the outputs are expected to match in both ETAP simulation and pre-lab calculations. Overall, this experiment reinforced concepts such as fault modeling, generator subtransient behavior, or the importance of transformer connections and grounding practices in the study of power systems analysis.

#### References

Toronto Metropolitan University. (n.d.). ELE 746 Laboratory Manual – Project 2: Three-Phase Symmetrical Faults, Department of Electrical Engineering [PDF]. D2L. https://courses.torontomu.ca/d2l/le/content/1076725/viewContent/6674498/View